## Sheet1
Document number: 2041901
WebPower Notes: Change history, Known problems, Compability matrix and build Tips & Tricks
Changes from Ver xx.xx to 3.0 (09.08.2006)
This is the first revision of SmartPackDist (402407.003) and below are the changes from which software it is based on (402048.003) SW WebPower std standalone (SB72).
General:
All support for AEON and MCU is removed and Webpower now supports distributed and standalone smartpack systems.
Tunneling:
Power suite can now connect through ethernet to smartpack via Webpower. Uses UDP protocol and port# 4002.
WEB:
Upgraded high contrast WEB design with white background.
Alarm and status windows now uses coloured background in addition to text to display the status.
Support for distributed systems include “alarms status & input monitor” and ‘battery bank monitor’ for up to 8 separate system controllers.
A new rectifier status window is added.
Improved alarm log view with xml file download. (Identical file format to powersuitet).
SNMP:
A new mib with support for distributed systems includes:
- A table with programmable inputs from up to 8 smartpacks.
- A table with symmetry inputs for 8 smartpacks.
Updated trapsystem. For the programmable inputs there is one trap for each controller, and variable binding for input identification.
Changes from Ver3.0 to 3.1 (15.12.2006)
Web page and SNMP are now able to show 27 bytes long rectifier Description/Name without crashing.
SNMP now reads and uses correct ‘community string’.
SNMP Traps now sends correct ‘enterprise oid’ in traps.
Changes from Ver3.1 to 4.0 (22.06.2007)
Completely new WEB interface, similar to Powersuite.
SNMP V2c. Traps are now in V2c format, and have some additional variable binding. The trap name text field is removed and a counter for repetitive traps was added, in addition to a variable holding info about control unit number where for digital inputs traps.
A warmstart trap and a authentication trap is added.
Due to the changes in the trapformat a new MIB file is made.
Changes from Ver4.0 to 4.1 (26.03.2008)
New SNMP functionality:
-HeartBeatTrap
-ResetManualAlarms command
-UserConfigurabletext (also in traps)
-ResetCtrlSystem command
-NumberOfStrings
-SymmetryInput values
-BatteryCapacitydata (time to disconnect, capacity left, capacity used, capacity total, battery quality)
-BatteryMonitorUnits (number of units, symmetry status, symmetry input value, fuse status, temperature)
-Major & Minor high temperature alarm levels.
-The MIB, “EltekDistributedPowerPlantV3.MIB”, is revised and updated with the new OID’s.
New WEB functionality:
- Reorganized the power explorer treeview. A separate input and output group show the logic inputs and outputs. The physical structure of the system is now shown in a 'Controlsystem' group.
- The 'Controlsystem' group in the power explorer contains an overview of physical units with type, partnumber, version number, serial number, software part number and software version number.
- A new detailed battery test logdata Window. logdata may be copied and pasted to A csv formatted textfile
- The Prog input status table in 'Inputs'->Smartpackxx' now contains enable/disable config setting for each input. Inputs used in symmetry measurements are flagged as 'Not Available'.
- The Batterybank input status table in 'Battery'->BatteryBankxx' now contains enable/disable config setting for each symmetry input. Inputs used as Configurable inputs are flagged as 'Not Available'.
- Battery monitor units are now displayed in The power explorer view along with The battery banks.
- Event log has added A progress bar graph | In some cases it can take up to 90 seconds to get the data if you need to get info via Can bus. The progress bar would inform the customer that it is a progress even if it is slow.
- The active Alarms view, now contains a button to reset all active alarms
- The Sites Text also appears in The browsers titlebar. A favicon also appears in The browsers addressline.
- The 'Power summary" view is reorganized, more status, and 3 ac phases added.
- The following status flags is visible if they are active:
*TempComp Enable/disable
*Charge Current Limit ON/OFF
*EffMan En/Dis
*Battery Time Left/Remaining Capacity.
*ON Battery
-Automatic update of power explorer navigator menu. The refresh button is removed, and the treeview/status colours utdate automatically.
-Values with no info from Smartpack should is now replavced by a '-'. This is done to make it clearer that we have no actual data to show in that form field.
Changes from Ver4.1 to 4.2 (23.04.2008)
Corrected bugs in writing default values during startup.
Changes from Ver4.2 to 4.3 (1.7.2009)
New SNMP functionality:
-Added support for I/O monitor control units.
-Temperature traps
-Delta Fanspeed traps
-Programmable Input traps
-Temperature values
-Fanspeed and delta fanspeed values
-Programmable input texts and status
-Added support for Load monitor control units.
-Fuse status
-Current values
MIB Info:
-"EltekDistributedPowerPlantV4.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
-"EltekDistributedPowerPlantV4_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
-"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
New WEB functionality:
-Added new webpages for Load monitor control units.
-Added Temperature handler tab to Smartpack 'Input' Webpage for Smartpacks that support this.
-Changed login system. There are now 10 named user accounts. Three access levels; STATUS,CONTROL,ADMIN. All Accounts can be added or deleted by administrator. User can change their own password.
-Added Map coordinates for use with automatic geographic placement and identification, in google/microsoft map applications.
-A new Online help button is placed on the top button bar. The URL is configured in the Network setup menu.
-Improved speed on web content using better cache control. Graphics, script, styles and html code is cached in the browser for faster response. Xml data is not cached in the browser.
-Improved speed of data read and write, The internal protocol between the webcontroller and the Smartpacks main CPU is optimized, thus speeding up data traffic.
-Faster update of webmenu when system status changes. The colours of the sidebar menu items updates faster. Discovery of new or removed items is also improved.
-Battery capacity data will show in percent or Ah depending on Smartpack setting.
-All relevant temperatures will show as Fahrenheit of centigrade depending on Smartpack setting.
-Rectifier Configuration webpage is redesigned. Added Emergency Voltage, and Generator dependant startup delay. 'HE' priority selection in Efficiency management setting is also new.
-A new EV-IPsetup program for configuration, software download and Web access for Eltek networkeded system controllers.
-To improve identification of individiual systems using EV-IPsetup, the 'Device Name' found in 'Network Setup' webpage will appear as a part of the full device name in the list of systems in EV IPsetup.
Known Issues:
Ref 3741:
WEB: On version 1.0 of Smartpack, ghost can nodes may appear. The number of ghost nodes of each type
will typically be the same as the number of Smartpack units. The ghost units will show in Controlsystem -
ControlUnit overview, Inputs – Input Overview, and load, Inputs, Battery and Output sidebar navigator.
Ref 3738:
Telnet: The hidden menu will not always be displayed. On rare occations, automatic printout of the
hidden diagnostics meny does not occur. The menu can however easily be displayed by typing a ‘?’.
Ref 3742:
WEB: Smartpack sw version 1.00 to 2.00 battery test results window will display wrong value for End voltage.
Ref 3745:
WEB: On smartpack version 1.00 and 1.02, battery test results may not show at all.
Ref 3744:
WEB: On smartpack version 1.00 and 1.02 symmetry tab will not show on battery bank window.
Ref 3743:
WEB: On Smartpack version 1.00, Rectifier summary window will show error for current share status
when there is no current share fault.
Changes from Ver4.3 to 4.5 (14.07.2010)
Updated NetBurner library
Changes from Ver4.5 to 4.6 (22.12.2010)
New funtionality:
Ref TT4259
-WEB: Added SSL login in web interface.
Ref TT4258
-WEB: Added json protocol support for communication with "Multisite monitor".
Ref TT4242
-WEB: Added NetBios protocol. Device name is now recognized on the network.
Ref TT4240
-SNMP: Solarchargers are now supported through SNMP. This includes 2 new traps as well, minor and major solarcharger trap.
Ref TT4238
-WEB: Added NTP (Network Time Protocol). The system clock can be updated from a timeserver on the network. Configuration through web interface.
Ref TT3968
- WEB: Added mains monitor web page with status and energy log.
- WEB: Added generator web page with status, configuration and energy log.
- WEB: Added Solar web page with status and energy log.
- WEB: Added energy log to rectifier web page.
- WEB: Added energy log to load web page.
- WEB: Added energy log and discharge cycle log to battery web page.
Bug fix/improvements:
Ref TT4260:
-Improved ARP protocol handling.
Ref TT4256
-Rectifier utilisation trap and status on webpage now works.
Ref TT4255
-Fixed xml parser incompatibility with Google Chrome browser making it possible to save values using Chrome browser.
Ref TT4253
-Fixed erroneous text on "programmable inputs" in "off-traps".
Ref TT4252
-Illegal values in energy log is now not shown in web interface.
Ref TT4248
-"Online help" url is now shown in web interface (Network config menu) without manually refreshing the page.
Ref TT4247
-Temperature unit Celsius or Fahrenheit is now shown correctly according to configuration in web header.
Ref TT4245
-Fixed erroneous status on load bank icon in menu tree.
Ref TT4244
-Fixed erroneous status of can node in "Control Unit Overview" if node was not present.
Ref TT4239
-Changed "On Battery" criterias. A threshold will now be calculated dependent on battery capacity and if generator is enabled or not. The red color is also removed when active.
Webpower 4.6 is tested and approved with the following Web browsers on MS Windows XP:
• | Microsoft IE 8
• | Mozilla Firefox 3
Known Issues:
Google Chrome browser will not work running SSL.
Ref 3741:
WEB: On sw version 01.00 of Smartpack, ghost can nodes may appear. The number of ghost nodes of each type
will typically be the same as the number of Smartpack units. The ghost units will show in Controlsystem -
ControlUnit overview, Inputs – Input Overview, and load, Inputs, Battery and Output sidebar navigator.
Ref 3742:
WEB: On Smartpack sw version 01.00 to 02.00, battery test results window will display wrong value for End voltage.
Ref 3745:
WEB: On smartpack sw version 01.00 up to 01.03, battery test results may not show at all.
Ref 3744:
WEB: On smartpack sw version 01.00 up to 01.03, symmetry tab will not show on battery bank window.
Ref 3743:
WEB: On Smartpack sw version 01.00, Rectifier summary window will show error for current share status
when there is no current share fault.
MIB Info:
-"EltekDistributedPowerPlantV5.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
-"EltekDistributedPowerPlantV5_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
-"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.6 to 4.7 (20.05.2011)
New functionality:
Ref TT3670
-WEB: "Model" field in "DC Plant Information" page is now editable.
Ref TT3764
-WEB: Added analog values for programmable inputs for both SmartPack and IO Unit.
Ref TT4162
-WEB: Added support for SmartNode in "Control Unit Overview".
Ref TT4304
-WEB: Added support for 2 more temperature inputs for SmartPack.
Ref TT3770
-SNMP: Added "Servicemode" function. If activated, traps will be disabled and relays will not operate.
Ref TT4280
-SNMP: Added Rectifier capacity minor and major traps.
Ref TT4279
-EMAIL: "Alarm Off" events will now trigger sending of mail if "Send Off Traps" ticker is activated under "Network Config-SNMP".
Bug fix/improvements:
-Built on new toolchain version 2.5.2
Ref TT4286
-WEB: Fixed problem with "ghost" battery monitors in tree view.
Ref TT3704
-WEB: "Test Mode" under "Rectifier-Configuration-Efficiency" is now under "admin" password level.
Ref TT2017
-WEB: Removed timestamp in eventlog "Description" field for certain messages.
Ref TT4308
-WEB: Corrected format of values and improved design of status web page for mains monitors.
Ref TT4303
-WEB: Fixed saving of values for LVLD monitor.
Ref TT4301
-WEB: Fixed "First" button on "Rectifiers-Rectifier Status" page.
Ref TT4300
-WEB: Fixed detailed rectifier and status info.
Ref TT4312
-WEB: Fixed viewing of battery test results.
Ref TT4313
-WEB: Changed unit text for "Delay after disconnect" from "min" to "second(s)".
Ref TT4314
-WEB: Added sdupport for desi ampere in battery monitor and Mains monitor.
Ref TT4324
-WEB: Changed format for generator run hours.
Ref TT4287
-SNMP: Fixed trap repeat for "alarmACMainsTrap".
Ref TT4298
-SNMP: Fixed traps for IO Units 9-14.
Ref TT4279
-EMAIL: Fixed format of email preventing it to be sent in certain cases.
Ref TT4311
-NTP accept replies from timeservers without any value in the "stratum" field.
Webpower 4.7 is tested and approved with the following Web browsers:
•IE8 (XP)
•IE9 (Windows 7)
•Firefox 4.0.1 (XP)
Known Issues:
Google Chrome browser will not work running SSL.
Ref 3741:
WEB: On sw version 01.00 of Smartpack, ghost can nodes may appear. The number of ghost nodes of each type
will typically be the same as the number of Smartpack units. The ghost units will show in Controlsystem -
ControlUnit overview, Inputs – Input Overview, and load, Inputs, Battery and Output sidebar navigator.
Ref 3742:
WEB: On Smartpack sw version 01.00 to 02.00, battery test results window will display wrong value for End voltage.
Ref 3745:
WEB: On smartpack sw version 01.00 up to 01.03, battery test results may not show at all.
Ref 3744:
WEB: On smartpack sw version 01.00 up to 01.03, symmetry tab will not show on battery bank window.
Ref 3743:
WEB: On Smartpack sw version 01.00, Rectifier summary window will show error for current share status
when there is no current share fault.
MIB Info:
"EltekDistributedPowerPlantV7.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV7_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.7 to 4.8 (19.09.2013)
New functionality:
Ref TT4338
-WEB: Added possibility to test timeserver connection and update time manually.
Bug fix/improvements:
-Built on new toolchain version 2.5.3
Ref TT4326
-SNMP: Fixed format on OID SystemTimeTime, the year was missing.
Ref TT4329
-SNMP: RFC1213-bug: Made sysName, sysContact or sysLocation OID writable.
Ref TT4361
-SNMP: Fixed bug in "RectifierCapacity" OID's.
Ref TT4330
-WEB: Updated JSON service to latest including "Function_Update".
Ref TT4335
-WEB: Fixed NAT issue with Login link.
Ref TT4340,TT4342, TT4343, TT4344, TT4346, TT4348, TT4350, TT4352, TT4353, TT4356
-WEB: Added support for Chrome browser.
Ref TT4349
-WEB: Improved update of tree menu if several user are logged on.
Ref TT4354
-WEB: Added support for more temperature inputs.
Ref TT4355
-WEB: Fixed status for the correlation between Temperature and programmable inputs.
Ref TT4358
-WEB: Updated the online help URL.
Ref TT4362
-WEB: Fixed erroneous calculation for "ON BATTERY" indication.
Webpower 4.8 is tested and approved with the following Web browsers:
•IE9 Version 9.0.8112.16421(Windows 7)
•Firefox Version 23.0.1
•Chrome Version 29.0.1547.66 m
Known Issues:
Google Chrome browser will not work running SSL.
Ref 3741:
WEB: On sw version 01.00 of Smartpack, ghost can nodes may appear. The number of ghost nodes of each type
will typically be the same as the number of Smartpack units. The ghost units will show in Controlsystem -
ControlUnit overview, Inputs – Input Overview, and load, Inputs, Battery and Output sidebar navigator.
Ref 3742:
WEB: On Smartpack sw version 01.00 to 02.00, battery test results window will display wrong value for End voltage.
Ref 3745:
WEB: On smartpack sw version 01.00 up to 01.03, battery test results may not show at all.
Ref 3744:
WEB: On smartpack sw version 01.00 up to 01.03, symmetry tab will not show on battery bank window.
Ref 3743:
WEB: On Smartpack sw version 01.00, Rectifier summary window will show error for current share status
when there is no current share fault.
MIB Info:
"EltekDistributedPowerPlantV7.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV7_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.8 to 4.9 (23.01.2015)
Security update:
Security update:
TT4364: Implement new SSL certificate with 1024 bits encryption key
Bug fix:
TT4365: SSL lock up problem
TT4366: Problem to save rectifier configuration
TT4370: System configuration Map coordinates are not saved if using IE11
Cosmetic:
TT4368: Remove “Valere” from the Eltek logo
MIB:
*Stepped MIB version to V8.
*Removed traces of “Valere”.
*Updated revision history.
Web browser SSL prerequisites:
SSLV3 protocol must be enabled and allowed by browser
Known Issues:
Google Chrome browser does not work well over SSL.
MIB Info:
"EltekDistributedPowerPlantV8.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV8_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.9 to 4.10 (29.04.2015)
Bug fix:
TT4373 Erroneous NTP time sync occurs after approx. one year in operation.
Web browser SSL prerequisites:
SSLV3 protocol must be enabled and allowed by browser
Known Issues:
Google Chrome browser does not work well over SSL.
MIB Info:
"EltekDistributedPowerPlantV8.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV8_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.10 to 4.11 (01.04.2016)
New Functionality:
TT12298 Implement TLS protocol to make SSL work on newer browsers
TT12248 Add 3 battery test parameter settings for SNMP
NOTE: Target MCF5208 is no longer supported due to insufficient RAM
MIB Info:
"EltekDistributedPowerPlantV9.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV9_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
Changes from Ver4.11 to 4.12 (02.12.2016)
Improvements and bug fix:
TT12807 Web server breaks down when running an Nmap port scan
TT12822 Wrong ip address in alarm mail
TT12995 Warning for wrong format does not disappear
TT12998 The tree menu does not update properly
NOTE: Target MCF5208 is no longer supported due to insufficient RAM
MIB Info:
"EltekDistributedPowerPlantV9.MIB" is the complete mib tree. Use this if you have no previous Eltek mib in your NMS.
"EltekDistributedPowerPlantV9_branch9.MIB" is used if you already have "Eltek_Root.mib" compiled in your NMS together with other branches.
(Compiling several "x_branch9" mibs in your NMS will work fine since they are compatible. Dependant of the NMS the descriptions of OID's in the mib could be from either version)
"Eltek_Root.MIB" is the base mib-for all the branch-mibs. Hence, use it if you want to use several Eltek mibs simultaneously in your NMS.
3. Compability Matrix
WebPower Software | SmartPack Software | SmartPack Hardware
402413.003 Ver4.5 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402414.003 Ver4.5 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402413.003 Ver4.6 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402414.003 Ver4.6 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402413.003 Ver4.7 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402414.003 Ver4.7 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402413.003 Ver4.8 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402414.003 Ver4.8 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402413.003 Ver4.9 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402414.003 Ver4.9 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402413.003 Ver4.10 (MCF5208) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.113 V2.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.117 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.04, SW Smartpack dist. | 242100.118 V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.00, SW Smartpack dist. | 242100.118 V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.01, SW Smartpack dist. | 242100.118SC V1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.02, SW Smartpack dist. | 242100.118SC V2, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver03.03, SW Smartpack dist. | 242100.118SC V3, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402414.003 Ver4.10 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402414.003 Ver4.11 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402073.009 Ver03.10, SW Smartpack dist.
402414.003 Ver4.12 (MCF5235) | 402073.009 Ver02.00, SW Smartpack dist. | 242100.118 V3.x, SmartPackExtended with Web/SNMP (microcontroller MB90345)
| 402073.009 Ver02.03, SW Smartpack dist. | 242100.118SC V3.1, SmartPackExtended with Web/SNMP (microcontroller MB90345)
402073.009 Ver02.04, SW Smartpack dist.
402073.009 Ver03.00, SW Smartpack dist.
402073.009 Ver03.01, SW Smartpack dist.
402073.009 Ver03.02, SW Smartpack dist.
402073.009 Ver03.03, SW Smartpack dist.
402073.009 Ver03.04, SW Smartpack dist.
402073.009 Ver03.05, SW Smartpack dist.
402073.009 Ver03.06, SW Smartpack dist.
402073.009 Ver03.07, SW Smartpack dist.
402073.009 Ver03.08, SW Smartpack dist.
402073.009 Ver03.09, SW Smartpack dist.
402073.009 Ver03.10, SW Smartpack dist.